## Sheet1
Type | Read Input Register
FC | 0x04
No | Address | Name | Type | Unit | Description |  | Flag |  | feedback status |  | system status
1 | 0x1000 | ADS_Analog Ch0 | uint16 | x0.1 V | Load 1 Voltage |  | bit 0 | Undervoltage | bit 0 | MCB1 status, 1 = ON, 0 = OFF | bit 0 | run status, 0 = off, 1 = on
2 | 0x1001 | ADS_Analog Ch1 | uint16 | x0.1 V | Load 2 Voltage |  | bit1 | Overvoltage | bit 1 | MCB2 status, 1 = ON, 0 = OFF | bit 1 | mode, 0 = auto, 1 = manual
3 | 0x1002 | ADS_Analog Ch2 | uint16 | x0.1 V | Load 3 Voltage |  | bit 2 | Overcurrent | bit 2 | MCB3 status 1 = ON, 0 = OFF
4 | 0x1003 | ADS_Analog Ch3 | uint16 | x0.1 V | System Voltage |  | bit 3 | Short Cicuit | bit 3 | Relay 1 Status, 1 = ON, 0 = OFF
5 | 0x1004 | Analog Ch1 | int16 | x0.01 A | Load 1 Current |  |  |  | bit 4 | Relay 2 Status, 1 = ON, 0 = OFF
6 | 0x1005 | Analog Ch2 | int16 | x0.01 A | Load 2 Current |  |  |  | bit 5 | Relay 3 Status, 1 = ON, 0 = OFF
7 | 0x1006 | Analog Ch3 | int16 | x0.01 A | Load 3 Current |  |  |  | bit 6 | Relay on 1 failed
8 | 0x1007 | flag 1 | uint16 |  | flag channel 1 |  |  |  | bit 7 | Relay off 1 failed
9 | 0x1008 | flag 2 | uint16 |  | flag channel 2 |  |  |  | bit 8 | Relay on 2 failed
10 | 0x1009 | flag 3 | uint16 |  | flag channel 3 |  |  |  | bit 9 | Relay off 2 failed
11 | 0x1010 | feedback status | uint16 |  | MCB feedback status |  |  |  | bit 10 | Relay on 3 failed
12 | 0x1011 | system status | uint16 |  | system status |  |  |  | bit 11 | Relay off 3 failed
13 | 0x1012
14 | 0x1013
15 | 0x1014
Type | Read Holding Register
FC | 0x03
No | Address | Name | Type | Unit | Value | Description | Block
1 | 0x1000 | Baudrate | uint16 |  | 0 - 6 | Modbus baudrate | Communication setting | 0 = 9600, 1 = 14400, 2 = 19200, 3 = 28800, 4 = 38400, 5 = 57600, 6 = 115200
2 | 0x1001 | Id | uint16 |  | 1 - 254 | Device id
3 | 0x1002 | Overvoltage Disconnect 1 | uint16 | 0.1 V |  | Overvoltage disconnect voltage 1 | Load 1 Parameter
4 | 0x1003 | Overvoltage Reconnect 1 | uint16 | 0.1 V |  | Overvoltage reconnect voltage 1
5 | 0x1004 | Undervoltage Disconnect 1 | uint16 | 0.1 V |  | Undervoltage disconnect 1
6 | 0x1005 | Undervoltage Reconnect 1 | uint16 | 0.1 V |  | Unvervoltage reconnect voltage 1
7 | 0x1006 | Overcurrent Disconnect 1 | uint16 | 0.01 A |  | Overcurrent disconnect 1
8 | 0x1007 | Overcurrent Detection time delay 1 | uint16 | ms |  | Overcurrent detection time delay 1
9 | 0x1008 | Overcurrent Reconnect interval 1 | uint16 | ms |  | Overcurrent reconnect time delay 1
10 | 0x1009 | Short Circuit Disconnect 1 | uint16 | 0.01 A |  | Short circuit disconnect 1
11 | 0x1010 | Short Circuit Detection time delay 1 | uint16 | ms |  | Short circuit detection time delay 1
12 | 0x1011 | Short Circuit Reconnect interval 1 | uint16 | ms |  | Short circuit reconnect time delay 1
13 | 0x1012 | Output Mode 1 | uint16 |  | 0 - 1 | Output Mode (source / sink), 0 = source, 1 = sink
14 | 0x1013 | Overvoltage Disconnect 2 | uint16 | 0.1 V |  | Overvoltage disconnect voltage 2 | Load 2 Parameter
15 | 0x1014 | Overvoltage Reconnect 2 | uint16 | 0.1 V |  | Overvoltage reconnect voltage 2
16 | 0x1015 | Undervoltage Disconnect 2 | uint16 | 0.1 V |  | Undervoltage disconnect 2
17 | 0x1016 | Undervoltage Reconnect 2 | uint16 | 0.1 V |  | Unvervoltage reconnect voltage 2
18 | 0x1017 | Overcurrent Disconnect 2 | uint16 | 0.01 A |  | Overcurrent disconnect 2
19 | 0x1018 | Overcurrent Detection time delay 2 | uint16 | ms |  | Overcurrent detection time delay 2
20 | 0x1019 | Overcurrent Reconnect interval 2 | uint16 | ms |  | Overcurrent reconnect time delay 2
21 | 0x1020 | Short Circuit Disconnect 2 | uint16 | 0.01 A |  | Short circuit disconnect 2
22 | 0x1021 | Short Circuit Detection time delay 2 | uint16 | ms |  | Short circuit detection time delay 2
23 | 0x1022 | Short Circuit Reconnect interval 2 | uint16 | ms |  | Short circuit reconnect time delay 2
24 | 0x1023 | Output Mode 2 | uint16 |  | 0 - 1 | Output Mode (source / sink), 0 = source, 1 = sink
25 | 0x1024 | Overvoltage Disconnect 3 | uint16 | 0.1 V |  | Overvoltage disconnect voltage 3 | Load 3 Parameter
26 | 0x1025 | Overvoltage Reconnect 3 | uint16 | 0.1 V |  | Overvoltage reconnect voltage 3
27 | 0x1026 | Undervoltage Disconnect 3 | uint16 | 0.1 V |  | Undervoltage disconnect 3
28 | 0x1027 | Undervoltage Reconnect 3 | uint16 | 0.1 V |  | Unvervoltage reconnect voltage 3
29 | 0x1028 | Overcurrent Disconnect 3 | uint16 | 0.01 A |  | Overcurrent disconnect 3
30 | 0x1029 | Overcurrent Detection time delay 3 | uint16 | ms |  | Overcurrent detection time delay 3
31 | 0x1030 | Overcurrent Reconnect interval 3 | uint16 | ms |  | Overcurrent reconnect time delay 3
32 | 0x1031 | Short Circuit Disconnect 3 | uint16 | 0.01 A |  | Short circuit disconnect 3
33 | 0x1032 | Short Circuit Detection time delay 3 | uint16 | ms |  | Short circuit detection time delay 3
34 | 0x1033 | Short Circuit Reconnect interval 3 | uint16 | ms |  | Short circuit reconnect time delay 3
35 | 0x1034 | Output Mode 3 | uint16 |  | 0 - 1 | Output Mode (source / sink), 0 = source, 1 = sink
Type | Read Coil Status
FC | 0x02
No | Address | Name | Type | Unit | Value | Description | Block
1 | 0x1000 | Relay 1 ON | bool |  | 0 - 1 | 1 to activate
2 | 0x1001 | Relay 1 OFF | bool |  | 0 - 1 | 1 to activate
3 | 0x1002 | Relay 2 ON | bool |  | 0 - 1 | 1 to activate
4 | 0x1003 | Relay 2 OFF | bool |  | 0 - 1 | 1 to activate
5 | 0x1004 | Relay 3 ON | bool |  | 0 - 1 | 1 to activate
6 | 0x1005 | Relay 3 OFF | bool |  | 0 - 1 | 1 to activate
7 | 0x1006 | Manual Mode | bool |  | 0 - 1 | 0 = auto, 1 = manual
8 | 0x1007 | Restart | bool |  | 0 - 1 | 0 = idle, 1 = restart
9 | 0x1008 | Factory Reset | bool |  | 0 - 1 | 1 = reset to factory setting
10 | 0x1010
11 | 0x1011
12 | 0x1012
13 | 0x1013
14 | 0x1014
15 | 0x1015
16 | 0x1016
17 | 0x1017
18 | 0x1018
19 | 0x1019
20 | 0x1020
21 | 0x1021
22 | 0x1022
23 | 0x1023
Type | Write Holding Register
FC | 0x10
No | Address | Name | Type | Unit | Value | Description | Block
1 | 0x1000 | Baudrate | uint16 |  | 0 - 6 | Modbus baudrate | Communication setting | 0 = 9600, 1 = 14400, 2 = 19200, 3 = 28800, 4 = 38400, 5 = 57600, 6 = 115200
2 | 0x1001 | Id | uint16 |  | 1 - 254 | Device id
3 | 0x1002 | Overvoltage Disconnect 1 | uint16 | 0.1 V |  | Overvoltage disconnect voltage 1 | Load 1 Parameter
4 | 0x1003 | Overvoltage Reconnect 1 | uint16 | 0.1 V |  | Overvoltage reconnect voltage 1
5 | 0x1004 | Undervoltage Disconnect 1 | uint16 | 0.1 V |  | Undervoltage disconnect 1
6 | 0x1005 | Undervoltage Reconnect 1 | uint16 | 0.1 V |  | Unvervoltage reconnect voltage 1
7 | 0x1006 | Overcurrent Disconnect 1 | uint16 | 0.01 A |  | Overcurrent disconnect 1
8 | 0x1007 | Overcurrent Detection time delay 1 | uint16 | ms |  | Overcurrent detection time delay 1
9 | 0x1008 | Overcurrent Reconnect interval 1 | uint16 | ms |  | Overcurrent reconnect time delay 1
10 | 0x1009 | Short Circuit Disconnect 1 | uint16 | 0.01 A |  | Short circuit disconnect 1
11 | 0x1010 | Short Circuit Detection time delay 1 | uint16 | ms |  | Short circuit detection time delay 1
12 | 0x1011 | Short Circuit Reconnect interval 1 | uint16 | ms |  | Short circuit reconnect time delay 1
13 | 0x1012 | Output Mode 1 | uint16 |  | 0 - 1 | Output Mode (source / sink), 0 = source, 1 = sink
14 | 0x1013 | Overvoltage Disconnect 2 | uint16 | 0.1 V |  | Overvoltage disconnect voltage 2 | Load 2 Parameter
15 | 0x1014 | Overvoltage Reconnect 2 | uint16 | 0.1 V |  | Overvoltage reconnect voltage 2
16 | 0x1015 | Undervoltage Disconnect 2 | uint16 | 0.1 V |  | Undervoltage disconnect 2
17 | 0x1016 | Undervoltage Reconnect 2 | uint16 | 0.1 V |  | Unvervoltage reconnect voltage 2
18 | 0x1017 | Overcurrent Disconnect 2 | uint16 | 0.01 A |  | Overcurrent disconnect 2
19 | 0x1018 | Overcurrent Detection time delay 2 | uint16 | ms |  | Overcurrent detection time delay 2
20 | 0x1019 | Overcurrent Reconnect interval 2 | uint16 | ms |  | Overcurrent reconnect time delay 2
21 | 0x1020 | Short Circuit Disconnect 2 | uint16 | 0.01 A |  | Short circuit disconnect 2
22 | 0x1021 | Short Circuit Detection time delay 2 | uint16 | ms |  | Short circuit detection time delay 2
23 | 0x1022 | Short Circuit Reconnect interval 2 | uint16 | ms |  | Short circuit reconnect time delay 2
24 | 0x1023 | Output Mode 2 | uint16 |  | 0 - 1 | Output Mode (source / sink), 0 = source, 1 = sink
25 | 0x1024 | Overvoltage Disconnect 3 | uint16 | 0.1 V |  | Overvoltage disconnect voltage 3 | Load 3 Parameter
26 | 0x1025 | Overvoltage Reconnect 3 | uint16 | 0.1 V |  | Overvoltage reconnect voltage 3
27 | 0x1026 | Undervoltage Disconnect 3 | uint16 | 0.1 V |  | Undervoltage disconnect 3
28 | 0x1027 | Undervoltage Reconnect 3 | uint16 | 0.1 V |  | Unvervoltage reconnect voltage 3
29 | 0x1028 | Overcurrent Disconnect 3 | uint16 | 0.01 A |  | Overcurrent disconnect 3
30 | 0x1029 | Overcurrent Detection time delay 3 | uint16 | ms |  | Overcurrent detection time delay 3
31 | 0x1030 | Overcurrent Reconnect interval 3 | uint16 | ms |  | Overcurrent reconnect time delay 3
32 | 0x1031 | Short Circuit Disconnect 3 | uint16 | 0.01 A |  | Short circuit disconnect 3
33 | 0x1032 | Short Circuit Detection time delay 3 | uint16 | ms |  | Short circuit detection time delay 3
34 | 0x1033 | Short Circuit Reconnect interval 3 | uint16 | ms |  | Short circuit reconnect time delay 3
35 | 0x1034 | Output Mode 3 | uint16 |  | 0 - 1 | Output Mode (source / sink), 0 = source, 1 = sink
| 0x2000 | Start Upload Firmware | 0 - 64 registers |  | raw hex value | maximum 128 bytes data | Address for OTA upload purpose
| 0x2001 | Start Upload Flash | 0 - 64 registers |  | raw hex value | maximum 128 bytes data
| 0x2002 | Upload Process | 0 - 64 registers |  | raw hex value | maximum 128 bytes data
| 0x2003 | End Upload | 0 - 64 registers |  | raw hex value | maximum 128 bytes data
| 0x2004 | Start Upload Compressed Firmware | 0 - 64 registers |  | raw hex value | maximum 128 bytes data
| 0x2005 | Start Upload Compressed Flash | 0 - 64 registers |  | raw hex value | maximum 128 bytes data
| 0x2006 | Upload Compressed Process | 0 - 64 registers |  | raw hex value | maximum 128 bytes data
| 0x2007 | End Upload Compressed | 0 - 64 registers |  | raw hex value | maximum 128 bytes data